## Sheet1
Residential Service Inspection Checklist (NEC 2023) | Name: | Date:
General Service Entrance | Address:
• Service Rating:
Verify service entrance conductors and main service disconnect are appropriately rated for the dwelling's electrical load.
• Service Conductors:
- Conductor Sizing: Verify that service conductors are sized according to NEC 2023 Table 310.16. Ensure the conductors are capable of carrying the full
load of the service and meet the minimum ampacity requirements based on the insulation type, conductor material (copper or aluminum), and the installation conditions.
•230.24(A) through ( E ) clearances for systems not over 1,000 volts nominal are met.
•230.26 Point of attachment. The point of attachment of the overhead service conductors to a building or other structure shap providethe minuim clearances specified in 230.9 and 230.24. In no case shall this point of
attachment be less than (10 ft) above finished grade.
•230.51(A) Service enterance cabels. Service Enterance cabels shall be supported by straps or other approved means within (12 in) of every service head, goose neck, or connection to a raceway or enclosure and at
intervals not exceeding (30 in).
•230.54(F) Drip Loops. Drip loops shall be formed on the individual conductors. To prevent the enterance of moisture, service-enterance conductors shall be connected to the service drop or over head service conductors
either (1) below the level of the service head, (2) below the level of the termination of the cable enterance sheath.
352.30(A) PVC conduit shall be securly fastened within (3 ft) of each outlet box, junction box, conduit body, or other conduit termination. Conduit listed for securing at other than (3 ft) shall be permitted to be installed
in accordance with the listing.
- Conductor Insulation:
Confirm that the service conductors have the appropriate insulation type (e.g., THHN, THWN-2) for the installation environment (e.g., wet, dry, or direct burial).
- Temperature Rating:
Ensure that the conductors are selected based on their temperature rating and that derating factors 310.15(B)(1), 310.15©(1) are applied if conductors are installed in conditions that exceed the standard
ambient temperature.
• Service Disconnect:
Confirm that the main service disconnect is located in a readily accessible location outside the building or nearest the point of entrance of the service conductors.
• Service Grounding:
- Grounding Electrode Conductor Sizing: Ensure that the grounding electrode conductor is sized according to NEC Table 250.66, based on the size of the service-entrance conductors.
- Ground Electrode Placement: Confirm that grounding electrodes (e.g., ground rods, concrete-encased electrodes) are installed at the base of the moisture level for optimal grounding performance.
- Resistance Measurement: Verify that the resistance to ground is 25 ohms or less. If the resistance is higher, ensure a supplemental electrode is installed as required by NEC.
- Electrode Spacing: Ensure that if two ground electrodes are present (e.g., two ground rods), they are spaced at least 6 feet apart, as required by NEC 2023.
• Bonding
• General Bonding: Verify that all grounding and bonding conductors are correctly installed and connected to the service equipment.
• Secondary Bonding to Water Line: Ensure that the water line is bonded at two points—both before and after the water meter/main, using appropriate bonding clamps and jumpers.
• Bonding Clamps and Jumpers: Confirm that bonding clamps are installed at any location where PEX, Vega, or other non-metallic materials interrupt the continuity of the metal water piping system.
• NEC Table 250.122 Compliance: Verify that the bonding jumpers and conductors are sized according to NEC Table 250.122, ensuring proper sizing for the system's overcurrent protection.
Residential Service Inspection Checklist (NEC 2023) - Page 2
Service Panel
• Service Panel
• Panel Rating: Check that the service panel is correctly rated for the dwelling's electrical load (e.g., 100A, 200A).
• Panel Location: Ensure the service panel is installed in an accessible location, with clear working space of at least 30 inches wide, 36 inches deep, and 6.5 feet in height.
• Circuit Breakers: Inspect that circuit breakers are properly sized for the wire gauge and are not damaged.
• Labeling: Confirm all circuits are clearly and accurately labeled in the panel directory.
• Neutral Isolation: Ensure the neutral bus is isolated from the ground in subpanels.
• Grounding and Bonding: Verify that the panel's grounding and bonding are correctly done as per NEC guidelines, including compliance with bonding requirements as noted in the previous section.
•Branch Circuits
• Wiring Method: Inspect all wiring methods (e.g., NM cable, conduit) for compliance with NEC standards.
• Wire Sizing: Check that all branch circuit conductors are correctly sized based on the circuit's load and breaker size.
• Conductor Insulation: Ensure conductor insulation is appropriate for the environment and is undamaged.
• Overcurrent Protection: Verify that overcurrent protection devices (breakers/fuses) are properly rated for the conductors they protect.
• Arc-Fault Circuit Interrupters (AFCIs):
- AFCI Protection: Confirm AFCI protection is installed in all required areas, such as bedrooms, living rooms, and other habitable spaces as per NEC 2023 Section 210.12(A).
- 210.12(B) Compliance: Ensure that AFCI protection is extended to branch circuits supplying outlets or devices installed in kitchens, laundry areas, bathrooms, and similar spaces as required by NEC 2023 Section
•Ground-Fault Circuit Interrupters (GFCIs)
• GFCI Protection: Ensure GFCI protection is installed in required locations, including:
- Kitchens: All kitchen receptacles, including countertop outlets, appliance receptacles, and any receptacle within the kitchen area as per NEC 2023 Section 210.8(A)(7).
- Bathrooms, garages, basements (Section 210.8(A)(6)), and outdoor receptacles.
- Laundry Areas: Ensure that GFCI protection is installed for receptacles in laundry areas, as required by NEC 2023 Section 210.8(D). This includes receptacles for washing machines, dryers, and other
laundry-related appliances.
- Ranges and Cooktops: Ensure GFCI protection is installed for receptacles supplying power to ranges and cooktops in kitchen and cooking areas as required by NEC 2023 Section 210.8(D). Confirm that these appliances
are properly grounded, and that GFCI devices are correctly installed to provide protection.
•Lighting
• Fixture Ratings: Check that all light fixtures are rated for the environment (e.g., damp or wet locations) and for the installed bulb wattage.
• Grounding: Ensure all metal light fixtures are properly grounded.
• Switch Controls: Verify that lights are controlled by wall switches where required, and that dimmers or other controls are compatible with the installed lighting.
• Exterior Lighting Requirements (NEC 2023):
- Required Exterior Lighting Locations:
- Front and Back Entry/Exit Lighting (NEC 210.70(A)(2)(b)): Confirm that exterior lighting is installed at all entry/exit doors, including the front and rear of the dwelling. This includes ensuring that a switch-controlled
lighting outlet is installed at these locations.
- Detached Garages and Other Accessory Buildings (NEC 210.70(A)(2)(b)): Ensure that a lighting outlet is installed to provide illumination for the exterior of detached garages and other accessory buildings
with electrical power.
- Basement and Attic Exterior Access (NEC 210.70(A)(3)): Verify that lighting is provided at exterior entrances to basements and attics where access is from the outside.
- Fixture Requirements: Ensure that exterior lighting fixtures are suitable for wet or damp locations, as required by NEC 2023 Section 410.10(A).
- Switch Location: Verify that a wall switch is installed to control exterior lighting at all entry/exit points, as required by NEC 2023 Section 210.70(A)(2)(b).
- Protection and Accessibility: Ensure all exterior lighting and associated wiring are properly protected from physical damage and are installed in a manner that maintains accessibility for maintenance and replacement.
Fixed Electric Space Heating Equipment (NEC 2023 Section 424)
•424.4(B)Branch-Circuit condctor sizing. The branch-circuit conductor ampacity shall not be less than 125% of the load of the fixed electric space-heating equipment and any associated motors.
•424.6 Listed Equipment. Electric baseboard heaters, heatingcacables, duct heaters, and radiant heating systems shall be listed and labeled.
•424.11 Supply Conductors. Fixed electric space heating equipment requiring supply conductors grater than 60C shall be clearly and permanently marked. This marking shall be plainly visible after installation and shall
be permitted1 to be adjacent to the field connection box.
•424.19©Unit Swith(es) as disconnectiong means. A unit switch(es) with a marked "off" position that is part of a fixed heater and disconnects all ungrounded conductors shall be permitted as the disconnecting means
required by this article where other means for disconnection are provided in occupancies in 424.19© through ©(4)
•423.4(A) Branch circuits supplying two or more outlets for fixed electric space-heating equipment shall not be rated over 30 amperes.
•424.45 € Ground-fault circuit-interrupter protection. In adedition to the requirements in 210.8, ground-fault circuit interrupter protection for personell shall be provided.
Doorbell Requirements (NEC 2023 Section 725.121 and Section 725.41)
• Power Source (NEC 725.121): Ensure that the doorbell transformer is powered from a listed Class 2 power source, and verify that it is properly protected and installed according to NEC 2023 requirements.
• Wiring Method (NEC 725.41): Confirm that doorbell wiring is installed using appropriate low-voltage wiring methods and is protected from physical damage. Verify that the wiring is properly routed and secured
in compliancewith NEC 2023 Section 725.41.
• Location and Protection: Ensure that the doorbell components, such as the chime and transformer, are located in accessible areas and are protected from damage, as specified by NEC 2023.